## Sheet1
| Equip. | Inspection | H2 | CH4 | C2H2 | C2H4 | C2H6 | CO | CO2 | fault
0 | U | Low energy partial discharges and x-wax formation | 32930 | 2397 | 0 | 0 | 157 | 313 | 560 | 0
1 | I | Corona and x-wax formation | 37800 | 1740 | 8 | 8 | 249 | 56 | 197 | 0
2 | I | X-wax deposition | 92600 | 10200 | 0 | 0 | 0 | 6400 | 103151 | 0
3 | B | Partial discharges inducing displacement of insulation and bolt | 8266 | 1061 | 0 | 0 | 22 | 107 | 498 | 0
4 | I | Partial discharges | 9340 | 995 | 7 | 6 | 60 | 60 | 620 | 0
5 | I | X-wax deposits | 36036 | 4704 | 10 | 5 | 554 | 6 | 347 | 0
6 | I | X-wax deposits | 33046 | 619 | 0 | 2 | 58 | 51 | 1 | 0
7 | I | X-wax deposits | 40280 | 1069 | 1 | 1 | 1060 | 1 | 0 | 0
8 | P | Loosening of potential ring on bushing, with marks of sparking and tracking | 78 | 20 | 28 | 13 | 11 | 0 | 784 | 1
9 | P | Sparking between HV braided connection and isolated copper tube | 305 | 100 | 541 | 161 | 33 | 440 | 3700 | 1
10 | S | Selector breaking current in selector tank | 35 | 6 | 482 | 26 | 3 | 200 | 2240 | 1
11 | U | Continuous sparking between metal cups and earthed bolts in winding | 543 | 120 | 1880 | 411 | 41 | 76 | 2800 | 1
12 | P | Tracking to HV bushing | 1230 | 163 | 692 | 233 | 27 | 130 | 115 | 1
13 | P | Tracking in bushing | 645 | 86 | 317 | 110 | 13 | 74 | 114 | 1
14 | R | Tracking to the ground in glue of central beam | 60 | 10 | 4 | 4 | 4 | 780 | 7600 | 1
15 | P | Sparking on tank walls to the bushing | 95 | 10 | 39 | 11 | 0 | 122 | 467 | 1
16 | S | 500 OLTC normal operations | 6870 | 1028 | 5500 | 900 | 79 | 29 | 388 | 1
17 | S | 3600 OLTC normal operations | 10092 | 5399 | 37565 | 6500 | 530 | 42 | 413 | 1
18 | 0 | Poor shielding contact (electrical problem) | 650 | 81 | 270 | 51 | 170 | 380 | 2000 | 1
19 | C | Traces of discharges in paper of cone junction of HV cable | 210 | 22 | 7 | 6 | 6 | 19 | 74 | 1
20 | R | Sparking from bushing to tank | 385 | 60 | 159 | 53 | 8 | 465 | 1250 | 1
21 | R | Sparking from bushing to tank | 4230 | 690 | 1180 | 196 | 5 | 438 | 791 | 1
22 | R | Tracking in paper | 7600 | 1230 | 1560 | 836 | 318 | 4970 | 4080 | 1
23 | P | Low energy arcing on bushing | 595 | 80 | 244 | 89 | 9 | 524 | 2100 | 1
24 | R | Low energy in core | 120 | 25 | 40 | 8 | 1 | 500 | 1600 | 1
25 | S | Contamination from OLTC | 8 | 0 | 101 | 43 | 0 | 192 | 4067 | 1
26 | R | Tracking in insulation | 6454 | 2313 | 6432 | 2159 | 121 | 3628 | 225 | 1
27 | R | Tracking from windings to beam | 2177 | 1049 | 705 | 440 | 207 | 4571 | 3923 | 1
28 | R | Sparking / Tracking in insulation | 1790 | 580 | 619 | 336 | 321 | 956 | 4250 | 1
29 | P | Sparking from core to ground | 1330 | 10 | 182 | 66 | 20 | 231 | 1820 | 1
30 | U | Contamination from OLTC | 4 | 1 | 52 | 7 | 2 | 93 | 519 | 1
31 | U | Defective OLTC operation | 1900 | 285 | 7730 | 957 | 31 | 681 | 732 | 1
32 | B | Low energy arcing in bushing | 57 | 24 | 30 | 27 | 2 | 540 | 2518 | 1
33 | P | Flahover from LV to ground, external | 440 | 89 | 757 | 304 | 19 | 299 | 1190 | 2
34 | S | Arc in selector switch | 210 | 43 | 187 | 102 | 12 | 167 | 1070 | 2
35 | U | Short circuit in distribution windings | 2850 | 1115 | 3675 | 1987 | 138 | 2330 | 4330 | 2
36 | U | Short circuit from LV to ground, internal | 7020 | 1850 | 4410 | 2960 | 0 | 2140 | 1000 | 2
37 | P | Short circuit from LV to connector | 545 | 130 | 239 | 153 | 16 | 660 | 2850 | 2
38 | P | Arcing from windings to porcelain | 7150 | 1440 | 1760 | 1210 | 97 | 608 | 2260 | 2
39 | U | Tertiary windings damaged by arcing | 620 | 325 | 244 | 181 | 38 | 1480 | 2530 | 2
40 | R | Arcing in wet cellulose | 120 | 31 | 94 | 66 | 0 | 48 | 271 | 2
41 | P | Short circuit in windings | 755 | 229 | 460 | 404 | 32 | 845 | 5580 | 2
42 | R | Arcing from windings to ground (inadvertent piece leftover) | 5100 | 1430 | 1010 | 1140 | 0 | 117 | 197 | 2
43 | U | Short circuit in windings | 13500 | 6110 | 4040 | 4510 | 212 | 8690 | 1460 | 2
44 | P | Bushing swollen, tank opened | 1570 | 1110 | 1830 | 1780 | 175 | 135 | 602 | 2
45 | P | Arcing to magnetic circuit (ground) | 3090 | 5020 | 2540 | 3800 | 323 | 270 | 400 | 2
46 | P | Short circuit between conductors | 1820 | 405 | 634 | 365 | 35 | 1010 | 8610 | 2
47 | R | Arcing inside windings | 535 | 160 | 680 | 305 | 16 | 172 | 338 | 2
48 | U | Flash-over between dislocated connection and HV bushing turret | 13 | 3 | 6 | 3 | 1 | 4 | 51 | 2
49 | U | Flash-over due to lightning overvoltage with burnt insulation and leads | 137 | 67 | 104 | 53 | 7 | 196 | 1678 | 2
50 | S | Arcing on selector switch ring | 1084 | 188 | 769 | 166 | 8 | 38 | 199 | 2
51 | U | Arcing between connections to tap changer, burnt areas on windings | 34 | 21 | 56 | 49 | 4 | 95 | 315 | 2
52 | I | Arcing in static shield connections | 7940 | 2000 | 5390 | 3120 | 355 | 1130 | 285 | 2
53 | C | Very short HV high energy discharge, followed by tracking | 150 | 130 | 30 | 55 | 9 | 120 | 200 | 2
54 | R | Arcing from bushing to tank | 8200 | 3790 | 5830 | 4620 | 250 | 31 | 85 | 2
55 | P | Arcing in windings | 260 | 215 | 277 | 334 | 35 | 130 | 416 | 2
56 | P | Arcing in windings | 75 | 15 | 26 | 14 | 7 | 105 | 322 | 2
57 | R | Arcing in windings | 530 | 345 | 250 | 266 | 85 | 3900 | 20000 | 2
58 | P | Arcing in oil | 60 | 5 | 21 | 21 | 2 | 188 | 2510 | 2
59 | R | Arcing in wndings | 90 | 28 | 32 | 31 | 8 | 1380 | 11700 | 2
60 | R | Arcing in wndings | 220 | 77 | 240 | 170 | 22 | 1800 | 13800 | 2
61 | R | Arcing in wndings | 5900 | 1500 | 2300 | 1200 | 68 | 750 | 335 | 2
62 | U | Arcing in wndings | 420 | 250 | 800 | 530 | 41 | 300 | 751 | 2
63 | R | Arcing from bushing to tank | 2800 | 2800 | 3600 | 3500 | 234 | 92 | 718 | 2
64 | R | Arcing in bushing | 99 | 170 | 190 | 200 | 20 | 140 | 1160 | 2
65 | U | Arcing in oil duct | 310 | 230 | 760 | 610 | 54 | 150 | 631 | 2
66 | U | Arcing in oil duct | 800 | 160 | 600 | 260 | 23 | 490 | 690 | 2
67 | P | Arcing from bushing to tank | 1500 | 395 | 323 | 395 | 28 | 365 | 576 | 2
68 | P | Arcing from windings to core | 20000 | 13000 | 57000 | 29000 | 1850 | 2600 | 2430 | 2
69 | R | Arcing in windings (molten metal) | 305 | 85 | 130 | 197 | 25 | 813 | 8380 | 2
70 | R | Arcing in windings | 1900 | 530 | 434 | 383 | 35 | 1890 | 7570 | 2
71 | R | Arcing in windings | 110 | 62 | 250 | 140 | 90 | 680 | 6470 | 2
72 | P | Arcing in oil (turret) | 3700 | 1690 | 3270 | 2810 | 128 | 22 | 86 | 2
73 | P | Arcing in oil (turret) | 2770 | 660 | 763 | 712 | 54 | 522 | 1490 | 2
74 | R | Arcing from bushing to tank | 245 | 120 | 167 | 131 | 18 | 829 | 4250 | 2
75 | P | Arcing from HV to tank | 1170 | 255 | 325 | 312 | 18 | 5 | 1800 | 2
76 | R | Arcing from bushing to tank | 4419 | 3564 | 2025 | 2861 | 668 | 909 | 9082 | 2
77 | R | Arcing in bushing | 810 | 580 | 490 | 570 | 111 | 1100 | 6800 | 2
78 | R | Arcing in bushing insulation | 5000 | 1200 | 1100 | 1000 | 83 | 140 | 265 | 2
79 | U | Arcing in OLTC and windings | 10000 | 6730 | 10400 | 7330 | 345 | 1980 | 3830 | 2
80 | P | High circulating currents between conductors with winding damage | 1270 | 3450 | 8 | 1390 | 520 | 483 | 44500 | 3
81 | P | Circulating currents in LV windings and core | 3420 | 7870 | 33 | 6990 | 1500 | 573 | 4640 | 3
82 | I | Thermal runaway inside thick insulation with puncture / carbonization of paper | 360 | 610 | 9 | 260 | 259 | 12000 | 74200 | 3
83 | I | Thermal runaway in thick paper insulation | 1 | 27 | 1 | 4 | 49 | 53 | 254 | 3
84 | U | Blackened area within windings, interturn fault, open circuit parallel path | 3675 | 6392 | 5 | 7691 | 2500 | 101 | 833 | 3
85 | P | Vertical bar buses burnt out, carbonization of paper strips | 48 | 610 | 0 | 10 | 29 | 1900 | 970 | 3
86 | P | Carbonized windings during heat run tests | 12 | 18 | 0 | 4 | 4 | 559 | 1710 | 3
87 | P | Circulating currents in magnetic tank shunt during heat run tests | 66 | 60 | 0 | 7 | 2 | 76 | 90 | 3
88 | U | Overheating of core to ground and insulation shields (narrow oil ducts) | 1450 | 940 | 61 | 322 | 211 | 2420 | 3560 | 3
89 | B | Hot spot with carbon formation | 0 | 18900 | 330 | 540 | 410 | 3900 | 710 | 3
90 | I | Hot spot in paper | 960 | 4000 | 6 | 1560 | 1290 | 15800 | 50300 | 3
91 | I | Hot spot in paper | 24700 | 61000 | 1560 | 42100 | 26300 | 14400 | 30400 | 3
92 | P | Overheating of conductor < 200 °C | 14 | 44 | 1 | 7 | 124 | 128 | 2746 | 3
93 | R | Low temperature overheating of clamping beams of yokes by stray flux | 2031 | 149 | 0 | 3 | 20 | 556 | 3008 | 3
94 | R | Idem, with carbonization of beams | 480 | 1075 | 0 | 1132 | 298 | 464 | 1000 | 3
95 | B | Thermodielectric failure | 40000 | 400 | 6 | 600 | 70 | 800 | 218 | 3
96 | P | Hot spot at connection | 8800 | 64064 | 0 | 95650 | 72128 | 290 | 90300 | 4
97 | P | Circulating currents between yoke clamps and connecting bolts | 6709 | 10500 | 750 | 17700 | 1400 | 290 | 1500 | 4
98 | S | Pyrolitic carbon growth between selector contacts | 1100 | 1600 | 26 | 2010 | 221 | 0 | 1430 | 4
99 | P | Steel lamination eroded | 290 | 966 | 57 | 1810 | 299 | 72 | 756 | 4
100 | P | Circulating currents in clamping bolt | 2500 | 10500 | 6 | 13500 | 4790 | 530 | 2310 | 4
101 | U | Contacts of selector switch burnt | 1860 | 4980 | 1600 | 10700 | 0 | 158 | 1300 | 4
102 | U | Lengthy overheating of tap changer contacts | 860 | 1670 | 40 | 2050 | 30 | 10 | 690 | 4
103 | U | Defects on contacts of tap changer selector | 150 | 22 | 11 | 60 | 9 | 0 | 0 | 4
104 | P | High contact resistance of winding terminal | 400 | 940 | 24 | 820 | 210 | 390 | 1700 | 4
105 | P | Ground wiring burnt and ruptured by circulating current | 6 | 2990 | 67 | 26076 | 29990 | 6 | 26 | 4
106 | U | Burnt copper contacts in change over selector | 100 | 200 | 11 | 670 | 110 | 100 | 650 | 4
107 | P | Bad contact in windings | 290 | 1260 | 8 | 820 | 231 | 228 | 826 | 4
108 | R | Bad contact in defective weld in windings | 1550 | 2740 | 184 | 5450 | 816 | 1140 | 9360 | 4
109 | R | Hot spots in laminations | 3910 | 4290 | 1230 | 6040 | 626 | 1800 | 11500 | 4
110 | R | Hot spot in laminations (molten steel) | 12705 | 23498 | 5188 | 34257 | 6047 | 4004 | 8539 | 4
111 | R | Hot spot on bushing | 1 | 8 | 6 | 100 | 8 | 300 | 5130 | 4
112 | R | High temperature in laminations | 300 | 700 | 36 | 1700 | 280 | 760 | 9250 | 4